# ABSORPTION MACHINES	MS. 1

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | All absorption machines must be serviced in accordance with the manufacturer's detailed servicing instructions. Only manufacturer's specified parts are to be used | EACH VISIT |  |
| 2 | Start up and commissioning must be carried out in accordance with the manufacturer's instructions and must conform to the job specifications. | ANNUALLY |  |

# AIR COOLED CONDENSERS	MS. 2

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of condenser by reading compressor discharge pressure and determining corresponding temperature. | EACH VISIT |  |
| 2 | Check operation and condition of fans. |  |  |
| 3 | Inspect fan and motor bearings and lubricate as necessary |  |  |
| 4 | Check and adjust where necessary fixtures and mounts. |  |  |
| 5 | Inspect for free airflow through the condenser. |  | Abnormally high head pressure can indicate lack of proper air flow |
| 6 | Check operation of head pressure control dampers, if applicable |  |  |
| 7 | Report abnormally high noise level. |  |  |
| 8 | Inspect coil and fins |  |  |
| 9 | Inspect for rust |  |  |
| 10 | Measure full load motor amps and compare with nameplate | ANNUALLY | Watch for any fractured bakelite |
| 11 | Calibrate head pressure controller and notched linkage arms |  |  |
| 12 | Report on general condition of equipment |  |  |
| 13 | Report all defects |  |  |

# AIR DISTRIBUTION SYSTEMS	MS. 3

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect accessible high pressure ductwork for leaks. | EACH VISIT |  |
| 2 | Inspect and adjust as necessary all dampers and linkages. |  |  |
| 3 | Inspect and report on general condition of all plantroom ductwork, external insulation and support brackets including any undue corrosion. |  |  |
| 4 | Inspect access door gaskets, hinges, locks and handles. |  |  |
| 5 | Report all defects |  |  |

# AIR DRYERS	MS. 4

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Clean condenser coil | EACH VISIT | Adhere to manufacturer's operating instructions & take special note of control operating pressure settings |
| 2 | Note operation in accordance with manufacturer's instructions |  |  |
| 3 | Drain moisture, where applicable |  |  |
| 4 | Inspect filter operation |  |  |
| 5 | Leak test the system | ANNUALLY |  |

# BOILERS (Steam, Oil, Gas)	MS. 5

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check boiler operation | QUARTERLY |  |
| 2 | Carry out tube clean and inspection and report | ANNUALLY |  |
| 3 | Report all defects | QUARTERLY |  |

# CENTRIFUGAL	MS. 6

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of machine and record all items on Planned | EACH VISIT |  |
| 2 | Record number of starts of purge pump if counter is fitted |  | If counter not fitted submit report. This gives a positive indication of air in |
| 3 | Inspect moisture level in purge chamber sight glass. |  | Drain as necessary |
| 4 | Record pre-lube and post-lube timing of oil pump. |  |  |
| 5 | Inspect for undue noise and vibration |  |  |
| 6 | Inspect for oil leaks |  |  |
| 7 | Report general machine condition and clean |  |  |
| 8 | Calibrate safety and operating controls | ANNUALLY | Seal off control settings |
| 9 | Check operation of oil - refrigerant separation system |  |  |
| 10 | Megger motor windings of:- a) Main Motor b) Purge Recovery |  | DO NOT MEGGER MOTORS UNDER VACUUM |
| 11 | Inspect purge compressor valves & replace as authorised |  |  |
| 12 | Clean float and purge chamber & strainer, test float |  | Report any necessary repairs or replacements |
| 13 | Clean condenser tubes internally |  | Report scale deposits which cannot be removed |
| 14 | Report any tube plate corrosion |  | Do not paint tube plates. Do not use sharp pointed tools to remove tube plate |
| 15 | Start machine and commission |  |  |
| 16 | Analyse refrigerant and oil |  | Have samples tested and submit report by industrial chemist |
| 17 | Test operation of purge system |  |  |
| 18 | Clean plant room area and report general machine condition |  |  |

# COILS AND SPRAYS	MS. 7

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect coils for damaged fins and build up of dirt or lint | EACH VISIT |  |
| 2 | Inspect sprays and clean as necessary |  |  |
| 3 | Inspect for unnecessary bypass around coil and report |  |  |
| 4 | Check for overspray and report |  |  |
| 5 | Inspect coil eliminators and report |  |  |
| 6 | Check for damaged spray nozzles | ANNUALLY | Replace as necessary only with the identical nozzle type. If nozzle type unavailable, replace all nozzles. |
| 7 | Inspect and report on spray piping |  |  |
| 8 | Report general condition of equipment |  |  |

# COMPUTER PROCESS COOLING UNITS	MS. 8

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | AIR HANDLERS SECTION: Check fan rotation |  |  |
| 2 | Check all filters |  | Replace with factory approved type only |
| 3 | Inspect evap Coil |  | Clean if necessary |
| 4 | Clean condensate drain and tray | MONTHLY | Check 'S' bend and test drains with water |
| 5 | Lubricate motor bearings |  | Use high grade lubricants only |
| 6 | Check fan blade condition and clean |  | Ensure balance weights secured |
| 7 | Check fresh air intake fan |  | Clean filter is required |
| 8 | Check sail switch operation |  |  |
| 9 | AIR COOLED CONDENSERS OR TOWERS: Lubricate fan bearings | HALF/ YEARLY |  |
| 10 | Check drive belts | MONTHLY | Replace matched belts |
| 11 | Check fan condition |  |  |
| 12 | Check pump condition |  |  |
| 13 | Lubricate pump bearings |  |  |
| 14 | Check fan control operation |  | H.P. control with low ambient essential |
| 15 | Inspect coils of slats for scaling |  |  |
| 16 | Check water strainers, ball float & bleed rate |  | As required |
| 17 | COMPRESSORS: Check H.P. & L.P. control operation |  | Trip setting according to manufacturer's recommendations |
| 18 | Check suction and discharge pressures |  | Note any abnormalities |
| 19 | Check superheat setting | BI-MONTHLY | Process Cooling System/Superheat setting very important |
| 20 | Check crankcase heaters |  | Ensure heater is secured |
| 21 | Check pipework |  | Tighten bracket and saddles |
| 22 | ELECTRICAL: Check all motors for overheating | MONTHLY |  |

# COMPUTER PROCESS COOLING UNITS 	MS. 8 Continued…

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 23 | Check Amperage of all motors | MONTHLY | Compare actual/nameplate rating |
| 24 | Check all overloads and circuit breakers | HALF YEARLY | Tighten electrical connections |
| 25 | Inspect all relays, contactors and components | YEARLY |  |
| 26 | Check panel light operation |  | Use only factory replacements |
| 27 | HUMIDIFIERS: Check and clean reservoirs, drain and condensate trays | MONTHLY |  |
| 28 | Check heater elements/electrodes |  |  |
| 29 | Check scale deposits in bottles |  |  |
| 30 | Check current, salinity and control operation |  | Humitronic only adjust setting accordingly |
| 31 | Check inlet water strainers | MONTHLY | Clean as required. Note condition on mesh |
| 32 | Check drain cycle |  |  |
| 33 | Check steam distributor pipes |  |  |
| 34 | Check ball float and micro switches |  | Adjust accordingly/ensure correct operating water level |
| 35 | Check operation of solenoid valves |  |  |
| 36 | CONTROLS: Check setting of controls |  | Calibrate if temperature recorder indicates control swing |
| 37 | Check general condition |  |  |
| 38 | GENERAL: Check units for missing screws and locks |  |  |
| 39 | Check general overhaul condition of units |  |  |
| 40 | Clean units | MONTHLY | Vacuum clean all over |
| 41 | Any comments to be written on standard COMPANY report form |  |  |
| 42 | Inspect for rust, treat minor rust condition |  | Paint as necessary. Report on excessive deterioration |
| 43 | Check under floor condition | QUARTERLY | Report moisture and/or dust |
| 44 | Report any defects |  |  |

# CONDENSERS, WATER COOLED	MS. 9

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of condenser by reading compressor discharge pressure and determining corresponding temperature | EACH VISIT | See separate section headed "water treatment" |
|  | Shell & Tube And Shell & Coil |  |  |
| 2 | Check and adjust where necessary fixtures and mounts |  |  |
|  | Shell & Tube Condensers |  |  |
| 3 | Remove condenser water boxes | ANNUALLY |  |
| 4 | Clean condenser tubes |  | Report if nylon, bronze or other brush is used. Report on type of deposits in the condenser tubes by obtaining industrial chemist's analysis |
| 5 | Inspect tube plate for crevice corrosion & wire brush tube plates |  | Do not paint tube plates |
| 6 | Inspect water boxes for corrosion, especially in the division plate area |  |  |
| 7 | Replace division plate gasket |  | Use only manufacturer's recommended gasket material |
| 8 | Reassemble and test for refrigerant leaks |  |  |
| 9 | Clean condenser and general surrounding area |  |  |
| 10 | Report on general condition of equipment including paint finish |  |  |
|  | Shell & Coil Condensers |  |  |
| 11 | Inspect and report any corrosion at the water connections | ANNUALLY |  |
| 12 | Report on general condition of equipment including paint finish |  |  |

# CONTROL SYSTEMS	MS. 10

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Note the type of control system in operation, electric (voltage) pneumatic, electronic, and for what combination | EACH VISIT | Refer to Control Manufacturer's data for any specific setting alterations and/or adjustments |
| 2 | Measure and record condition space wet and dry bulb temperatures |  | Give controls time to settle down after adjustment has been carried out |
| 3 | Measure and record outdoor wet and dry bulb temperatures |  |  |
| 4 | Bleed moisture out of pneumatic system |  |  |
| 5 | Check operation of air compressor |  | See separate section headed "Air Compressors" |

# COOLERS, FLOODED & DIRECT EXPANSION	MS. 11

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of cooler by reading compressor suction pressure and determining corresponding temperature | EACH VISIT |  |
| 2 | Measure and record entering and leaving water temperatures |  |  |
| 3 | Check and adjust where necessary, fixtures and mounts |  |  |
| 4 | Inspect insulation and report |  |  |
| 5 | Inspect and record refrigerant level for flooded coolers |  |  |
| 6 | Inspect oil return on flooded coolers |  |  |
| 7 | Check operation of thermostatic expansion valves or levelmaster controls or float valves and king valve | ANNUALLY |  |
| 8 | Check operation of solenoid valves |  |  |
| 9 | Clean oil return strainer if necessary |  |  |
| 10 | Clean cooler and general surrounding area |  |  |
| 11 | Report on general condition of equipment including liquid suction heat interchanger |  |  |

# COOLING TOWERS	MS. 12

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check general tower operating condition | EACH VISIT |  |
| 2 | Check operation of distribution pan |  |  |
| 3 | Report on any water leaks |  |  |
| 4 | Check condition & operation of ball floats, adjust if necessary |  |  |
| 5 | Check the fan thermostat setting and adjust if necessary |  |  |
| 6 | Inspect pulleys and belts |  |  |
| 7 | Lubricate gear box and motor bearings as necessary |  | See separate sections headed "Pumps" |
| 8 | Check water treatment dosing system operation and tank level |  |  |
| 9 | Clean strainer |  |  |
| 10 | Check oil and top up level in gear box |  |  |
| 11 | Inspect for undue vibration and noise |  |  |
| 12 | Inspect to ensure free air flow with no recirculation |  | Report any abnormal conditions |
| 13 | Inspect for general unit corrosion & condition of slats & fill |  | Report fresh air intakes in relation to cooling tower discharge |
| 14 | Check security of bolts and fittings, adjust as necessary | ANNUALLY |  |
| 15 | Check security of drives and shaft assembly |  |  |
| 16 | Check motor bearings |  |  |
| 17 | Report on condition of equipment |  |  |

# DIESEL ENGINE	MS. 13

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect fuel tank for impurities and drain as necessary | EACH VISIT | Ensure engine is under manual control |
| 2 | Ensure fuel tank, radiator, crankcase are at full working level |  |  |
| 3 | Check pulleys and belts |  |  |
| 4 | Measure and record operating pressures and water temperatures |  | Operate engine to manufacturer's instructions |
| 5 | Inspect for oil and water leaks |  | Report as necessary |
| 6 | Check and report undue noise and vibration |  |  |
| 7 | Check engine exhaust smoke |  | Report any anomalies |
| 8 | Inspect engine heaters |  |  |
| 9 | Check unloading sequence and vibration during unloading |  |  |
| 10 | Check conditions of all pie and hose connections |  |  |
| 11 | Inspect generator performance |  | Consult manufacturer's instructions |
| 12 | Test safety controls and operation of controls | 6 MONTHLY | Operating pressures will indicate the need to clean strainer |
| 13 | Inspect suction strainer and clean if necessary |  | Follow manufacturer's recommendation |
| 14 | Drain, flush and refill radiator | ANNUALLY |  |
| 15 | Change engine oil |  | Use only oil specified by manufacturer |
| 16 | Grease or oil all lubrication points |  | Follow manufacturer's instructions |
| 17 | Replace or clean all filters as applicable |  | Use only manufacturer's specified parts |
| 18 | Check inlet and exhaust system. Tighten studs as necessary |  | Report on system leaks |
| 19 | Check fixtures and mountings |  |  |
| 20 | Check battery and clean as required |  |  |
| 21 | Check free air flow of plantroom intake screens, clean as necessary |  |  |
| 22 | Test run unit and switch to automatic operation |  | Operate to manufacturer's specifications |
| 23 | Report on general condition of equipment |  |  |

# ELECTRIC DUCT HEATERS	MS. 14

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check amperage per phase | PRE WINTER |  |
| 3 | Check control sequence |  |  |
| 4 | Check general operating condition | ANNUALLY | Before winter operation if applicable |
| 5 | Check fuses and fuse holders |  |  |

# ELECTRICAL SWITCHBOARDS & WIRING	MS. 15

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check for any burnt wiring and/or hot connections | EACH VISIT | Ensure power supply is disconnected prior to commencing work |
| 2 | Check for loose connections and tighten as necessary |  |  |
| 3 | Inspect all electrical meters |  | Report any malfunction |
| 4 | Inspect indicator lights |  |  |
| 5 | Inspect operation of time clocks and check settings |  | Report discrepancies. Allow for daylight saving. |
| 6 | Examine general condition of plantroom and outdoor conduit and connections. Report any undue corrosion |  | Ensure wiring diagrams are amended if necessary and stored in dry and dust free area |
| 7 | Inspect on/off switches for all equipment covered by contract |  |  |
| 8 | Check operation of variable speed drives if applicable. |  |  |
| 8 | Clean switchboard interior | ANNUALLY |  |
| 9 | Check and report on condition of exposed cable insulation |  |  |
| 10 | Inspect relays, circuit breakers, contactors and overloads |  |  |
| 11 | Inspect all fuses and fuse holders |  |  |
| 12 | Check operation of switchboard exhaust fan |  | See separate section headed "Fans" |
| 13 | Tidy switchboard area and report general operating condition |  |  |

# EMERGENCY BATTERIES	MS. 16

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check battery terminals for corrosion. Disconnect and clean if necessary with wire brush and apply pure petroleum jelly | EACHVISIT |  |
| 2 | Check battery cells and top up with distilled water as required |  | Use only distilled water when topping up batteries |
| 3 | Check specific gravity of batteries, readings should be approximately 1.16-1.25 |  |  |
| 4 | Check battery charging operation |  |  |
| 5 | Report on battery, and/or bank of batteries |  |  |

# EVAPORATIVE CONDENSERS	MS. 17

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Generally inspect condition of condenser | EACH VISIT | Replace as necessary only with the identical nozzle type |
| 2 | Clean and test spray nozzles |  | If nozzle type available, replace all nozzles |
| 3 | Test and adjust head pressure control |  |  |
| 4 | Test operation of pump and motor |  | See separate section headed "Pumps" |
| 5 | Check for undue noise and vibration |  | Submit report if necessary |
| 6 | Lubricate pump and motor bearings as necessary |  | See separate section headed "Pumps" |
| 7 | Check water strainer |  | Clean if necessary |
| 8 | Inspect canvas connections |  |  |
| 9 | Inspect pulleys and belts |  |  |
| 10 | Check fan and motor bearings for vibration and noise |  | Report any abnormal conditions |
| 11 | Tighten hanger bolts where necessary and inspect spring mounts for movement |  |  |
| 12 | Inspect operating water level and check and adjust ball floatas necessary |  |  |
| 13 | Inspect for scale on condenser coils and general unit corrosion |  | Report any undue corrosion |
| 14 | Drain and clean basin | QUARTERLY |  |
| 15 | Inspect coupling buffer material and replace if necessary | ANNUALLY |  |
| 16 | Check pulley alignment and correct as necessary |  |  |
| 17 | Lubricate all bearings |  |  |
| 18 | Report on general condition of equipment |  |  |

# EVAPORATIVE COOLERS (PACKAGED UNIT ONLY)	MS. 18

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check fan, motor and pump bearings and lubricate as necessary | EACH VISIT (SUMMER) |  |
| 2 | Inspect pulleys and belts |  |  |
| 3 | Check unit mounts, tighten as necessary |  |  |
| 4 | Inspect canvas connections |  |  |
| 5 | Inspect return air filters |  |  |
| 6 | Inspect water tank, spray nozzles and operation of ball float, clean nozzle as necessary |  |  |
| 7 | Check unit for undue corrosion. Apply paint when authorised |  | Use on odourless rust converter paint |
| 8 | Check fan and motor bearings and lubricate as necessary |  |  |
| 9 | Inspect pulleys and belts |  |  |
| 10 | Drain tank and clean pan | QUARTERLY |  |
| 11 | Clean fan |  | Inspect for out of balance fan assembly |
| 12 | Check electrical connections | ANNUALLY |  |
| 13 | Measure motor amps and compare with nameplate |  |  |
| 14 | Report on condition of external filters. Replace as authorised |  | Use on manufacturer's specified filters |

# FANS, CENTRIFUGAL & AXIAL	MS. 19

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect all bearings for lubrication, where applicable. Lubricate as necessary | EACH VISIT | Use lubricants as recommended by manufacturer |
| 2 | Inspect pulleys and belts |  |  |
| 3 | Check mounts and joints, and adjust if necessary |  |  |
| 4 | Check holding down bolts and tighten if necessary |  |  |
| 5 | Check spring mounts for undue vibration |  |  |
| 6 | Inspect canvas connections |  |  |
| 7 | Measure & record motor amperage, compare with nameplate rating |  | If ammeter not fitted use a tong tester |
| 8 | Check motor terminals |  | Watch for any fractured bakelite |
| 9 | Inspect for corrosion | ANNUALLY |  |
| 10 | Inspect door latches |  |  |
| 11 | Check out balance fan assemblies. Report as necessary |  | Free spin shaft & fans & watch for any sudden back spin action |
| 12 | Check guide vane assemblies where fitted |  |  |
| 13 | Inspect and report on the condition of insulation where fitted |  |  |
| 14 | Report on general condition of equipment |  |  |

NOTE:	Supply air, return air, smoke exhaust and spill air, incinerator exhaust systems, toilet exhaust, kitchen exhaust stair well pressurisation systems and general exhaust systems.

# FILTERS	MS. 20

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect and report on extent of sludge build up on oil bath filters | EACH VISIT | The manufacturer's service instructions must be followed particularly for electrostatic and absolute filters |
| 2 | Dry media filters are to be replaced where the media is starting to disintegrate or where the filter frame has fractured |  |  |
| 3 | Check operation of filter, motor, gears, lubricate as necessary |  |  |
| 4 | Check filter operating controls |  |  |
| 5 | Clean filters and oil where applicable |  |  |
| 6 | Check media winding movement |  |  |
| 7 | Check pressure drop across filter where suitable instruments are fitted |  |  |
| 8 | Report on general condition of filter |  |  |

# HOT WATER CALORIFIERS	MS. 21

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect unit for general operation | EACH VISIT |  |
| 2 | Inspect for leaks and report |  |  |
| 3 | Check all pipe connections |  |  |
| 4 | Inspect pump |  | See separate section headed "Pumps" |
| 5 | Measure and record operating pressures and temperatures |  |  |
| 6 | Check pump | SIX MONTHLY | See separate section headed "Pumps" |

# HUMIDIFIERS	MS. 22

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect general operation and clean nozzle | MONTHLY |  |
| 2 | Clean drain tray |  |  |
| 3 | Clean unit and electrode |  |  |
| 4 | Inspect and adjust as necessary the humidity controls |  | See separate section headed "Control Systems" |
| 5 | Clean water strainer |  |  |
| 6 | Check steam trap operation |  |  |
| 7 | Check pressure reducing valve and relief valve discharge |  |  |
| 8 | Check amperage of electrodes |  |  |
| 9 | Report general condition |  |  |

# TERMINAL UNITS	MS. 23

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check control operation, see manufacturer's instructions | EACH VISIT | Take particular note of hose connections and any deterioration in the rubber |
| 2 | Inspect for missing and broken discharge grilles |  |  |
| 3 | Ensure free air return and discharge |  |  |
| 4 | Report general condition of units | ANNUALLY |  |

# MIXING BOXES	MS. 24

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect general condition of mixing box and report | EACH VISIT |  |
| 2 | Check automatic controls | OR AS |  |
| 3 | Inspect dampers and linkages | APPLICABLE |  |
| 4 | Inspect insulation |  |  |
| 5 | Check for air leakage or bypass |  |  |

# PACKAGED UNITS	MS. 25

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect all bearings for lubrication, operating temperature and noise | EACH VISIT | Lubricate as necessary |
| 2 | Inspect pulleys and belts |  | Replace belts if worn |
| 3 | Check filters |  |  |
| 4 | Check fans |  |  |
| 5 | Inspect canvas connections |  | Replace as necessary |
| 6 | Inspect heating coils or heating elements |  |  |
| 7 | Inspect for any air leakage into unit cabinet |  | Ensure all panels properly fitted. |
| 8 | Inspect refrigeration system |  | See separate section headed "Refrigeration Compressors", "Condensers", "Refrigeration Piping and Controls" |
| 9 | Inspect electrical panel |  | See separate section headed "Electrical Switchboard and Wiring" |
| 10 | Measure full load amps on all motors and compare with nameplate rating |  |  |
| 11 | Complete check of all system controls |  | See separate section headed "Control Systems" |
| 12 | Check electrical switchboard |  | See separate section headed "Electrical Switchboard and Wiring" |
| 13 | Inspect insulation | ANNUALLY |  |
| 14 | Examine for corrosion |  | Report if replacement is considered necessary |
| 15 | Check refrigeration system |  | See separate section headed "Refrigeration Compressors", "Condensers", "Refrigeration Piping and Controls". |
| 16 | Check motor terminals |  | Watch for any fractured bakelite |
| 17 | Check pulley alignment |  |  |
| 18 | Report on general condition of equipment |  |  |

NOTE: Excluding compressors, condensers, electrical switchboards, refrigeration piping &controls

# PIPING SYSTEMS	MS. 26

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect the general condition of all accessible pipework - Insulation - Hangers - Valves - Cocks - Gauges - Brackets - Flexible Connectors | EACH VISIT |  |
| 2 | Tighten any accessible loose clamps, bolts or other fastenings |  | Do not use excessive tightening when working with visibly corroded pipe work |
| 3 | Inspect for leaks & Bleed air from system. |  |  |
| 4 | Report any undue noise and vibration |  |  |
| 5 | Inspect and report any undue corrosion |  |  |
| 6 | Report on faulty insulation | ANNUALLY |  |
| 7 | Report on general condition of accessible - Pipework - Fittings - General Pipework Supports |  |  |
| 8 | Inspect operation of all check valves |  |  |
| 9 | Inspect gate and globe valve glands |  |  |
| 10 | Inspect all flow switches |  |  |
| 11 | Report all defects |  |  |

NOTE: Chilled Water, Condenser water, hot water, brine & steam piping, but excluding refrigeration pipework.

# PLANTROOM	MS. 27

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Remove all waste materials | EACH VISIT |  |
| 2 | All machinery etc. to be kept in clean condition |  |  |
| 3 | Maintain floors in clean state |  |  |
| 4 | Replace lamps when necessary and maintain fittings in clean condition |  |  |
| 5 | Keep drains etc. free from waste material |  |  |
| 6 | Report on general condition of plantrooms |  |  |

# PUMPS	MS. 28

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of pump and motor | EACH VISIT | Record any matters requiring attention |
| 2 | Inspect pump gland and adjust if necessary |  |  |
| 3 | Test for undue noise and vibration |  |  |
| 4 | Inspect gland drain line |  |  |
| 5 | Check pump and motor bearings, lubricate as necessary. Check grease caps |  |  |
| 6 | Inspect pump and motor couplings for wear |  |  |
| 7 | Measure and record pump motor amperage. Compare with nameplate rating |  |  |
| 8 | Check operation of float switch control mechanism where fitted |  |  |
| 9 | Run standby pump where fitted |  |  |
| 10 | Inspect strainer and clean if necessary |  |  |
| 11 | Check coupling buffer material and coupling security |  |  |
| 12 | Check vibration isolators for any deterioration |  |  |
| 13 | Clean drain sumps |  |  |
| 14 | Check motor terminals |  | Watch for any fractured bakelite |
| 15 | Report all defects |  |  |

NOTE: Chilled water, condenser water, conditioner spray pumps, hot water, fuel oil, sump pumps, hydrant booster pumps

# REFRIGERATION COMPRESSORS RECIPROCATING	MS. 29

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Measure suction and discharge pressures and record pressures | EACH VISIT |  |
| 2 | Inspect pressure gauges |  | Report if gauges need replacement or repair |
| 3 | Observe unloading mechanism in relation to suction pressure, |  |  |
| 4 | Inspect and record oil level and pressure |  | Refer to manufacturer's data for correct operating oil pressures |
| 5 | Inspect condition of crankcase heaters in off position |  |  |
| 6 |  |  | Avoid over lubrication as this causes high bearing temperatures and |
| 7 | Check for refrigerant leaks |  |  |
| 8 | Check for undue noise and vibration |  |  |
| 9 | Inspect compressor motor coupling where fitted |  |  |
| 10 | Measure & record motor amperage. Compare with nameplate rating |  | If ammeter is not fitted, use tong tester |
| 11 | Run standby compressor where fitted |  | Where applicable, Items 1-12 apply |
| 12 | Check pulleys and belts where fitted |  | Ensure belts are not over tightened |
| 13 | Generally clean compressor motor assembly |  |  |
| 14 | Physically test compressor mounting springs or rubbers and | 6 MONTHLY |  |
| 15 | Simulate operation of compressor unloader mechanism |  |  |
| 16 | Check shaft seal for refrigerant leaks |  |  |
| 17 | Check all safety controls: H.P. & L.P. and oil safety | ANNUALLY | Report if any control needs replacement or repair |

# REFRIGERATION COMPRESSORS RECIPROCATING	MS. 29 Continued

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 18 | Lubricate and grease all points as necessary | ANNUALLY |  |
| 19 | Check solenoid unloading electrical connections |  |  |
| 20 | Analyse compressor motor oil report findings |  | This applies only to hermetic compressors |
| 21 | Test suction and discharge valves |  | This applies only to open compressors |
| 22 | Report any undue noise or vibration |  |  |
| 23 | Check compressor motor terminals |  | Watch for any fractured bakelite |
| 24 | Check alignment of compressor motor shafts |  | This applies only to open compressors |
| 25 | Report on general condition of equipment |  |  |
| 26 | Report all defects |  |  |

# REFRIGERATION PIPING & CONTROLS	MS. 30

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check condition of all refrigeration pipe work saddles | EACH VISIT | Check refrigeration pipework for any chafing. When silver soldering, do not use an oxidising flame. Use dry nitrogen where practical for purging pipework and/or systems. |
| 2 | Check suction line insulation and report if replacement is necessary |  |  |
| 3 | Check condition of vibration eliminators |  |  |
| 4 | Check operation of oil separator sump heater |  |  |
| 5 | Check operation of oil return through sight glass |  |  |
| 6 | Test temperature drop across the refrigerant drier. Report if drier blocked |  |  |
| 7 | Check operation of solenoid and thermostatic expansion valves |  |  |
| 8 | Check moisture indicators |  |  |
| 9 | Check super heat settings on thermostatic expansion valves | ANNUALLY |  |
| 10 | Inspect solenoid coils |  |  |
| 11 | Report all defects |  |  |

# ROOM AIR CONDITIONERS	MS. 31

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect unit for undue noise, vibration and corrosion | EACH VISIT | Report on general condition of unit |
| 2 | Check filters |  |  |
| 3 | Remove unit chassis from casing and:- - clean coils - clean fan blades - clean drain pan - check electrical connections - oil fan motor - comb fins as necessary - lubricate any linkages | ANNUALLY |  |
| 4 | Check fuse, three pin plug and power point |  | See separate section headed "Electrical Switchboards and Wiring". |
| 5 | Replace filter if major deterioration is evident |  |  |
| 6 | Report on general condition of unit |  |  |

# ROOM FAN COIL UNITS	MS. 32

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect all bearings for lubrication, operating temperatures and noise | EACH VISIT | Lubricate as necessary |
| 2 | Check filters | OR AS |  |
| 3 | Check fans | APPLICABLE |  |
| 4 | Check condition of coil for corrosion and lint, inspect condition of coil fins |  |  |
| 5 | Inspect heating elements |  |  |
| 6 | Inspect for any air leakage into unit cabinet |  | Ensure all panels properly fitted |
| 7 | Ensure free air return and discharge |  |  |
| 8 | Inspect for missing or broken discharge grilles |  |  |
| 10 | Check electrical wiring | ANNUALLY |  |
| 9 | Report general condition of unit |  |  |

# TANKS, WATER AND OIL FUEL	MS. 33

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
|  | Water Tanks |  |  |
|  | 1. Check operation and condition of float valve | EACH VISIT | Report any unusual increase or decrease in tank level |
|  | 2. Check condition of ball float |  |  |
|  | 3. Check and adjust if necessary water make up |  |  |
|  | 4. Check and clean overflow lines and drains |  |  |
|  | Oil Fuel Tanks |  |  |
|  | 1. Check daily oil tank for contents |  |  |
|  | 2. Check main storage tank vent and fillpoints are clear |  |  |
|  | 3. Check operation of main storage tank fuel gauge |  |  |
|  | Water Tanks |  |  |
|  | 1. Check for sludge and report | ANNUALLY |  |
|  | Oil Fuel Tanks |  |  |
|  | 1. Check for sludge |  |  |
|  | 2. Check for water and report |  |  |
|  | 3. Check operation of foot valve |  |  |
|  | 4. Check and recalibrate contents gauge if necessary |  |  |
|  | 5. Check and replace if necessary inspection hatch gaskets |  |  |
|  | 6. Report all defects |  |  |

# VARIABLE AIR VOLUME UNITS	MS. 34

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check operation of bellows | EACH VISIT | Ensure ceiling tiles are properly replaced. |
| 2 | Check plastic tube and connections | OR AS |  |
| 3 | Inspect controls and filter unit | APPLICABLE |  |

# WATER TREATMENT	MS. 35

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Take sample of condenser water | MONTHLY | For condenser water systems, treatment should control corrosion, organic fouling, amount of suspended solids, formation of scale and pH level. Legionella and Total Plate Counts to be taken and sent to laboratory for testing as required. |
| 2 | Test water ph and dissolved solids | MONTHLY | Upon testing adjustments to be made to bleed control where necessary to control scale and corrosion within condenser water system. Note to be taken of clarity of water within closed water circuits. |
| 3 | Test inhibitor levels | MONTHLY | The treatment should control corrosion and scale within condenser water and closed circuit systems. Dosing of inhibitors to be carried out where levels are below required set target levels to maintain effective treatment. |
| 4 | Monitor condition of cooling towers | MONTHLY | Check condition of cooling towers for signs of corrosion, scale and state of cleanliness. |
| 5 | Check operation of chemical dosing systems in use | MONTHLY | Monitor operation and make necessary adjustments. Dosing pumps and bleed systems to be checked for correct operation. Any faults to be noted on service report and action to be taken to rectify. |

# AIR COMPRESSORS RECEIVER	MS. 36

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check and adjust vee belt – replace if necessary | EACH VISIT | Check manufacturers lubrication recommendations |
| 2 | Check oil level and top up if necessary |  |  |
| 3 | Remove inlet air filter and replace if necessary |  |  |
| 4 | Check operation of controls |  |  |
| 5 | Check operation of receiver blow down/drain valve |  |  |
| 6 | Drain and replace oil to sump | ANNUALLY | Follow manufacturers recommendations |
| 7 | Open up receiver as required and prepare for annual inspection by licensed pressure vessel inspector |  |  |

# GENERAL	UPS. 01

| ITEM | PLANNED MAINTENANCE DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Check general condition of UPS enclosures | MONTHLY | Report on any damage where found |
| 2 | Visually inspect power components and electronic boards |  | Check for signs of overheating or mechanical stress |
| 3 | Check fans under power cells and roofs of cabinet |  | Check fans are rotating and free from mechanical stress |
| 4 | Inspect UPS environment |  | Check cleanliness and free of materials likely to cause fowling of UPS fans |
| 5 | Rectifier |  | Check and record A/C Voltage and Current draw to the rectifier. Check and record readings of DC Volts and Amps under load (at Panel). Check and record readings of charging Volts (with DVM). Visually check block and indication fault LED's for any abnormalities |
| 6 | Inverter |  | Check and record readings for A/C output volts with respect to each phase (if three phase output) and to Neutral. Check and record frequency on all phases. Visually check block and indication fault LED's for any abnormalities. |
| 7 | Static Switch |  | Check and record bypass voltage at S4 with respect to each other and to neutral. Visually check block and indication fault LED's for any abnormalities |
| 8 | Battery |  | Check battery connecting bus for oxidation, if present clean terminal and apply grease. If open cell batteries used, check electrolyte levels, top up as needed. Record which batteries require topping up. |
| 9 | UPS Display panel and remote mimic panel (if applicable) |  | Check green indicator is "ON", if amber or red condition exists, inform client. Check alarm history and record |
| 10 | Open Cell Batteries | QUARTERLY | Check specific gravity of electrolyte and record readings. Check and record floating voltage level of all batteries. Check UPS display panel and mimic panel (if appropriate) for correct functioning of LCD display. Clean all external surfaces of UPS. |
| 11 | With clients permission, simulate a mains failure | HALF YEARLY | Record the battery voltage for the autonomy of the UPS system and record readings at one minute interval. With oscilloscope monitor the output voltage and frequency of inverter. Check UPS panel to verify mains alarm was recorded. |
| 12 | With clients permission simulate a mains failure (cont'd) | HALF YEARLY | Ensure that working on battery critical discharge and end of |
| 13 | Test and tighten all electrical connections | ANNUALLY |  |
| 14 | Inspect all fuse holders and bases |  |  |
| 15 | Check and report on condition of all contractors and static |  |  |
| 16 | Check and report on current limitation safety on each output |  |  |
| 17 | Check and report on maximum and minimum voltage safety setpoints |  |  |
| 18 | Check and report on all bypass switching controls and safeties |  |  |
| 19 | Report all defects |  |  |

# AUSTRALIAN STANDARD AS3666 AND RELATED LEGISLATION	EHS-1

| ITEM | DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Inspect/report on condition of cooling tower/evaporative condensers | Annual | Report on cleanliness/deterioration |
| 2 | Inspect/Report on quality of filtration | Annual | Report any deterioration of filters |
| 3 | Inspect/Report on humidifiers, steam/spray - boiling/pan | Annual | Note - clean as necessary |
| 4 | Inspect coils, clean conditioner condensate trays, drains and flush | Annual | Clean and report on coil |
| 5 | Clean fresh air intake/exhaust grills | Annual | Clean to applicable standard |
| 6 | Clean fresh air/return air dampers | Annual | Clean to applicable standard |
| 7 | Vacuum clean internal conditioners housing | Annual | Dry vacuum, report any exceptional soiling |
| 8 | Clean coil/s | Annual | Clean coil |
| 9 | Inspect/report condition of air ducts in wet area's | Annual | Report on cleanliness/quote cleaning |
| 10 | Inspect/report on condition of air grills and registers | Annual | Report on condition |
| 11 | Inspect/report on cleanliness in hot water tanks | Annual | Report on condition/cleanliness |
| 12 | Clean plant room floor | Annual | Clean/report on contamination of all areas |
| 13 | Inspect terminal units(ie fan coil/induction unit). | Annual | Report on cleanliness |
| 14 | Warm water systems | Annual | Report and recommendations |
|  | PROVIDE CUSTOMER REPORT | ANNUAL | REPORT TO HIGHLIGHT NON COMPLIANCE TO AS3666 AND HEALTH LEGISLATION |

NOTE:	WHERE APPLICABLE, THIS BUILDING SERVICE SCHEDULE FORMS PART OF THE PLANNED PREVENTATIVE MAINTENANCE PROGRAM FROM COMPANY AUSTRALIA

# INDOOR BUILDING QUALITY AUDIT (I.E.Q.)	EHS-2

| ITEM | DESCRIPTION OF SERVICE | PERIOD | REMARKS |
| --- | --- | --- | --- |
| 1 | Review building operations, new equipment, refurbishment, absenteeism and complaints with superintendent | BI ANNUALLY | Modify inspection/audit/records accordingly |
| 2 | Check for abnormal odours and water ingression | BI ANNUALLY | Report any moulds, yeasts, fungus |
| 3 | Check for undue noise/vibrations, poor lighting | BI ANNUALLY | Identify source and report findings |
| 4 | TEMPERATURE/HUMIDITY Measure, record and calculate fresh air ventilation rate (Co2 method all floors) | BI ANNUALLY | Determine Co2 level and record |
| 5 | RESPIRABLE AND NUISANCE PARTICLES Measure and record dust level on each test location | BI ANNUALLY | Use laser beam particulate analyser and record level. Visually check coils and filters and report |
| 6 | MICROBIOLOGICAL CONTAMINATION Measure and record level of bacteria/yeast/moulds at fresh air intake and all handling units/zones | ANNUAL | Use "R.C.S." biological sampler, incubate, count and identify problem organisms |
| 7 | Measure and record level of bacteria/yeast/mould from carpets (as required) | ANNUAL | Take sample at microbial test locations. Use "Agar" surface sampling strips |
| NOTE | TEST RESULTS TO BE ANALYSED AND COMPARED TO IAQ STANDARDS, ANY RISK FACTORS AND THEIR IMPLICATIONS ARE TO BE REPORTED IN CONFIDENCE | ANNUAL | PROVIDE CUSTOMER REPORT AND ADVISE NON COMPLIANCE, RISK FACTOR. UTILISE PHOTOGRAPHIC EVIDENCE IF NECESSARY |

NOTE:	WHEN REFERENCING EHS-2 SCHEDULE TO COMPUTER ROOM SITES - ITEM 7 IS NOT APPLICABLE

# BUILDING MAINTENANCE SERVICE CHECK SHEET	EHR-1

 Denotes work carried out

|  | DESCRIPTION OF SERVICE |  | CLEAN | REMARKS |
| --- | --- | --- | --- | --- |
| 1 | Inspect/report on condition of cooling tower/evaporative condensers |  |  |  |
| 2 | Inspect/Report on quality of filtration |  |  |  |
| 3 | Inspect/Report on humidifiers, steam/spray - boiling/pan |  |  |  |
| 4 | Clean conditioner condensate trays, drains and flush |  |  |  |
| 5 | Clean fresh air intake/exhaust grills |  |  |  |
| 6 | Clean fresh air/return air dampers |  |  |  |
| 7 | Inspect and report on internal conditioners housing for cleanliness |  |  |  |
| 8 | Clean coil/s if necessary |  |  |  |
| 9 | Inspect/report condition of air ducts in wet area's |  |  |  |
| 10 | Inspect/report on condition of air grills and registers |  |  |  |
| 11 | Inspect/report on cleanliness in hot water tanks |  |  |  |
| 12 | Clean plant room floor |  |  |  |
| 13 | Inspect terminal units(ie fan coil/induction unit). |  |  |  |
| 14 | Inspect warm water systems, clean and report on tanks |  |  |  |
|  | PROVIDE CUSTOMER REPORT | ANNUAL | REPORT TO HIGHLIGHT NON COMPLIANCE TO AS3666 AND HEALTH LEGISLATION |  |

Date of service:	_________________________________	PM No:	______________________________

Maintenance Report No:	_________________________________	Serviceman's No:	______________________________

SERVICE SCHEDULE A
CENTRIFUGAL CHILLER

|  | LOCATION: |
| --- | --- |

"PREVENTATIVE MAINTENANCE PROGRAMME"

|  | MAINTENANCE TIME SCHEDULE |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SERVICE DETAILS: CENTRIFUGAL CHILLER | MONTHLY | BI-MONTHLY | QUARTERLY | HALF YEARLY | ANNUALLY |
| 1. RECORD DISCHARGE PRESSURE |  |  |  |  |  |
| 2. RECORD SUCTION PRESSURE |  |  |  |  |  |
| 3. RECORD OIL PRESSURE |  |  |  |  |  |
| 4. RECORD VOLTAGE READINGS |  |  |  |  |  |
| 5. RECORD COMPRESSOR AMP DRAW |  |  |  |  |  |
| 6. RECORD OIL PUMP AMP DRAW |  |  |  |  |  |
| 7. RECORD CHILLED WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 8. RECORD CONDENSER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 9. CHECK ELECTRICAL TERMINALS |  |  |  |  |  |
| 10. CHECK SUMP HEATER |  |  |  |  |  |
| 11. CHECK CONTACTOR AND RELAY OPERATION |  |  |  |  |  |
| 12. CHECK INLET VANE OPERATION |  |  |  |  |  |
| 13. CHECK POST LUBE TIMER OPERATION |  |  |  |  |  |
| 14. CHECK AND CALIBRATE MAIN TEMPERATURE CONTROLLER |  |  |  |  |  |
| 15. CHECK AND CALIBRATE SAFETY CONTROL OPERATION |  |  |  |  |  |
| 16. CHECK PURGE OPERATION |  |  |  |  |  |
| 17. CHECK FOR NOISE AND VIBRATION |  |  |  |  |  |
| 18. CHECK OIL TEMPERATURE TO BEARINGS |  |  |  |  |  |
| 19. CHECK REFRIGERANT CHARGE |  |  |  |  |  |
| 20. CHECK FOR OIL AND REFRIGERANT LEAKS |  |  |  |  |  |
| 21. LUBRICATE VANE LINKAGES |  |  |  |  |  |
| 22. CHECK REFRIGERANT TEMPERATURE |  |  |  |  |  |
| 23. STRIP AND CLEAN PURGE SYSTEM |  |  |  |  |  |
| 24. CLEAN CONDENSER |  |  |  |  |  |
| 25. OIL ANALYSIS CHECK |  |  |  |  |  |
| 26. REPLACE OIL FILTER |  |  |  |  |  |
| 27. REPLACE OIL & DRIER CORES |  |  |  |  |  |
| 28. FILL IN LOG SHEET |  |  |  |  |  |
| 29. DISCUSS OPERATION WITH OPERATOR |  |  |  |  |  |

SERVICE SCHEDULE B
RECIPROCATING CHILLER

|  | LOCATION: |
| --- | --- |

"PREVENTATIVE MAINTENANCE PROGRAMME"

|  | MAINTENANCE TIME SCHEDULE |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SERVICE DETAILS: RECIPROCATING CHILLER | MONTHLY | BI-MONTHLY | QUARTERLY | HALF YEARLY | ANNUALLY |
| 1. RECORD DISCHARGE PRESSURE |  |  |  |  |  |
| 2. RECORD SUCTION PRESSURE |  |  |  |  |  |
| 3. RECORD OIL PRESSURE |  |  |  |  |  |
| 4. RECORD VOLTAGE READINGS |  |  |  |  |  |
| 5. RECORD COMPRESSOR AMP DRAW |  |  |  |  |  |
| 6. RECORD CHILLER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 7. RECORD CONDENSER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 8. CHECK ELECTRICAL TERMINALS |  |  |  |  |  |
| 9. CHECK CRANKCASE HEATER |  |  |  |  |  |
| 10. CHECK CONTACTOR AND RELAY OPERATION |  |  |  |  |  |
| 11. CHECK OPERATION OF UNLOADERS |  |  |  |  |  |
| 12. CHECK PUMP DOWN OPERATION |  |  |  |  |  |
| 13. CHECK TX VALVE OPERATION AND SUPERHEAT |  |  |  |  |  |
| 14. CHECK CONTROL THERMOSTAT OPERATION |  |  |  |  |  |
| 15. CHECK AND CALIBRATE SAFETY CONTROLS OPERATION |  |  |  |  |  |
| 16. CHECK EXTERNAL INTERLOCKS OPERATION |  |  |  |  |  |
| 17. CHECK CONDENSER FANS (IF APPLICABLE) |  |  |  |  |  |
| 18. CHECK FOR NOISE AND VIBRATION |  |  |  |  |  |
| 19. CHECK FOR REFRIGERANT LEAKS |  |  |  |  |  |
| 20. CHECK FOR OIL LEAKS |  |  |  |  |  |
| 21. CHECK OIL LEVEL IN COMPRESSOR |  |  |  |  |  |
| 22. CLEAN CONDENSER |  |  |  |  |  |
| 23. OIL ANALYSIS CHECK |  |  |  |  |  |
| 24. REPLACE OIL CHANGE |  |  |  |  |  |
| 25. REPALCE DRIER CORES (IF APPLICABLE) |  |  |  |  |  |
| 26. FILL IN LOG SHEET |  |  |  |  |  |
| 27. DISCUSS OPERATION WITH OPERATOR |  |  |  |  |  |

SERVICE SCHEDULE C
HELICAL ROTARY CHILLER

|  | LOCATION: |
| --- | --- |

"PREVENTATIVE MAINTENANCE PROGRAMME"

|  | MAINTENANCE TIME SCHEDULE |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SERVICE DETAILS: HELICAL ROTARY CHILLER | MONTHLY | BI-MONTHLY | QUARTERLY | HALF YEARLY | ANNUALLY |
| 1. RECORD DISCHARGE PRESSURE |  |  |  |  |  |
| 2. RECORD SUCTION PRESSURE |  |  |  |  |  |
| 3. RECORD OIL PRESSURE |  |  |  |  |  |
| 4. RECORD VOLTAGE READINGS |  |  |  |  |  |
| 5. RECORD COMPRESSOR AMP DRAW |  |  |  |  |  |
| 6. RECORD CHILLER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 7. RECORD CONDENSER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 8. CHECK ELECTRICAL TERMINALS |  |  |  |  |  |
| 9. CHECK SUMP HEATER |  |  |  |  |  |
| 10. CHECK CONTACTOR AND RELAY OPERATION |  |  |  |  |  |
| 11. CHECK SLIDE VALVE OPERATION |  |  |  |  |  |
| 12. CHECK REFRIGERANT CHARGE |  |  |  |  |  |
| 13. CHECK METERING DEVICE OPERATION |  |  |  |  |  |
| 14. CHECK CONTROL THERMOSTAT OPERATION |  |  |  |  |  |
| 15. CHECK AND CALIBRATE SAFETY CONTROLS OPERATION |  |  |  |  |  |
| 16. CHECK EXTERNAL INTERLOCKS OPERATION |  |  |  |  |  |
| 17. CHECK CONDENSER FANS (IF APPLICABLE) |  |  |  |  |  |
| 18. CHECK FOR NOISE AND VIBRATION |  |  |  |  |  |
| 19. CHECK FOR REFRIGERANT LEAKS |  |  |  |  |  |
| 20. CHECK FOR OIL LEAKS |  |  |  |  |  |
| 21. CHECK OIL LEVEL IN COMPRESSOR |  |  |  |  |  |
| 22. CLEAN CONDENSER |  |  |  |  |  |
| 23. OIL ANALYSIS CHECK |  |  |  |  |  |
| 24. REPLACE OIL FILTER |  |  |  |  |  |
| 25. REPLACE OIL & DRIER CORES |  |  |  |  |  |
| 26. FILL IN LOG SHEET |  |  |  |  |  |
| 27. DISCUSS OPERATION WITH OPERATOR |  |  |  |  |  |

SERVICE SCHEDULE D
AIR COOLED CHILLERS

|  | LOCATION: |
| --- | --- |

"PREVENTATIVE MAINTENANCE PROGRAMME"

|  | MAINTENANCE TIME SCHEDULE |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SERVICE DETAILS: CENTRIFUGAL CHILLER | MONTHLY | BI-MONTHLY | QUARTERLY | HALF YEARLY | ANNUALLY |
| 1. RECORD DISCHARGE PRESSURE |  |  |  |  |  |
| 2. RECORD SUCTION PRESSURE |  |  |  |  |  |
| 3. RECORD OIL PRESSURE |  |  |  |  |  |
| 4. RECORD VOLTAGE READINGS |  |  |  |  |  |
| 5. RECORD COMPRESSOR AMP DRAW |  |  |  |  |  |
| 6. RECORD OIL PUMP AMP DRAW |  |  |  |  |  |
| 7. RECORD CHILLED WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 8. RECORD CONDENSER WATER TEMPERATURE IN/OUT |  |  |  |  |  |
| 9. CHECK ELECTRICAL TERMINALS |  |  |  |  |  |
| 10. CHECK SUMP HEATER |  |  |  |  |  |
| 11. CHECK CONTACTOR AND RELAY OPERATION |  |  |  |  |  |
| 12. CHECK INLET VANE OPERATION |  |  |  |  |  |
| 13. CHECK POST LUBE TIMER OPERATION |  |  |  |  |  |
| 14. CHECK AND CALIBRATE MAIN TEMPERATURE CONTROLLER |  |  |  |  |  |
| 15. CHECK AND CALIBRATE SAFETY CONTROL OPERATION |  |  |  |  |  |
| 16. CHECK PURGE OPERATION |  |  |  |  |  |
| 17. CHECK FOR NOISE AND VIBRATION |  |  |  |  |  |
| 18. CHECK OIL TEMPERATURE TO BEARINGS |  |  |  |  |  |
| 19. CHECK REFRIGERANT CHARGE |  |  |  |  |  |
| 20. CHECK FOR OIL AND REFRIGERANT LEAKS |  |  |  |  |  |
| 21. LUBRICATE VANE LINKAGES |  |  |  |  |  |
| 22. CHECK REFRIGERANT TEMPERATURE |  |  |  |  |  |
| 23. STRIP AND CLEAN PURGE SYSTEM |  |  |  |  |  |
| 24. CLEAN CONDENSER |  |  |  |  |  |
| 25. OIL ANALYSIS CHECK |  |  |  |  |  |
| 26. REPLACE OIL FILTER |  |  |  |  |  |
| 27. REPLACE OIL & DRIER CORES |  |  |  |  |  |
| 28. FILL IN LOG SHEET |  |  |  |  |  |
| 29. DISCUSS OPERATION WITH OPERATOR |  |  |  |  |  |